## Cover
AI CHECK SCOPE REGISTER — P&ID QUALITY & CONSISTENCY
One row per check from the Consolidated P&ID Checklist (358 checks), classified by AI execution feasibility, with Pass/Fail result columns for AI output and engineer disposition.
Project Name / No.:
Unit / Area:
P&ID Set / Revisions Checked:
Reference Document Revisions:
AI Tool / Model Used:
AI Run Date:
Engineer Reviewing AI Output:
Review Date:
AI FEASIBILITY CLASSES
AUTO | AI can execute end-to-end from the P&ID set plus reference registers (line list, instrument index, etc.); engineer verifies flagged findings.
ASSIST | AI extracts and compares data and flags candidate issues, but the check needs supplementary documents or engineering review to conclude.
HUMAN | Engineering judgment check — AI may summarize relevant drawing content, but must record the result as 'Not Checked' and leave the conclusion to the engineer.
RESULT CONVENTIONS
Pass | Check executed; no discrepancy found within AI's extraction confidence.
Fail | Candidate discrepancy found — details mandatory in 'AI Finding / Evidence' (sheet, tag, both values).
N/A | Check not applicable to this P&ID set / stage.
Not Checked | Not executed: HUMAN-class check, missing reference document, or illegible source — reason mandatory in Finding column.
Feasibility classes are pre-assigned defaults based on check content — the engineer may reclassify any row (dropdown provided). Every 'Fail' and every 'Not Checked' requires engineer disposition before drawing issue. AI findings are candidate discrepancies only; this register supplements, and does not replace, discipline squad check, inter-discipline review, and HAZOP.

## AI Check Register
AI CHECK SCOPE REGISTER
Check ID | Part | Section | Check Description | AI Feasibility | AI Result | AI Confidence | AI Finding / Evidence (sheet, tag, values) | Engineer Disposition
F-1.1 | Part A — Feed Stage | 1. GENERAL — DRAWING SET-UP, FORMAT & DOCUMENT CONTROL | P&ID set covers the full FEED scope: all process, utility, interconnecting, and relief/flare systems have a drawing; drawing index is complete. | ASSIST | Pass | High | Example: all 24 sheets present per index rev C; no gaps. Overwrite/delete before formal issue. | Accepted — J.S. 10-Jul-26
F-1.2 | Part A — Feed Stage | 1. GENERAL — DRAWING SET-UP, FORMAT & DOCUMENT CONTROL | Drawing numbering system, title block format, and revision scheme conform to project document control procedures. | ASSIST
F-1.3 | Part A — Feed Stage | 1. GENERAL — DRAWING SET-UP, FORMAT & DOCUMENT CONTROL | Legend & symbols sheets issued and P&IDs conform to them (ISA-5.1 / client standard); no undefined symbols. | ASSIST
F-1.4 | Part A — Feed Stage | 1. GENERAL — DRAWING SET-UP, FORMAT & DOCUMENT CONTROL | Drawing status (e.g., Issued for Design / Issued for HAZOP) correct; revision description and clouds reflect changes since last issue. | HUMAN
F-1.5 | Part A — Feed Stage | 1. GENERAL — DRAWING SET-UP, FORMAT & DOCUMENT CONTROL | All HOLDs are clouded, numbered, listed in a HOLD register/table with responsible party and target close-out phase. | ASSIST
F-1.6 | Part A — Feed Stage | 1. GENERAL — DRAWING SET-UP, FORMAT & DOCUMENT CONTROL | Continuation arrows/off-page connectors reference correct drawing numbers and are consistent in both directions. | ASSIST
F-1.7 | Part A — Feed Stage | 1. GENERAL — DRAWING SET-UP, FORMAT & DOCUMENT CONTROL | Battery limits and scope split (FEED contractor / licensor / vendor / existing facilities / by others) clearly shown and labelled. | ASSIST
F-1.8 | Part A — Feed Stage | 1. GENERAL — DRAWING SET-UP, FORMAT & DOCUMENT CONTROL | General notes established, applicable, and consistent across the P&ID set (typical details referenced rather than repeated). | ASSIST
F-1.9 | Part A — Feed Stage | 1. GENERAL — DRAWING SET-UP, FORMAT & DOCUMENT CONTROL | Licensor P&IDs / process design package (PDP) correctly transposed; deviations from licensor scheme documented and approved. | ASSIST
F-1.10 | Part A — Feed Stage | 1. GENERAL — DRAWING SET-UP, FORMAT & DOCUMENT CONTROL | P&IDs consistent with the approved PFDs and heat & material balance (stream data, equipment count, configuration). | ASSIST
F-1.11 | Part A — Feed Stage | 1. GENERAL — DRAWING SET-UP, FORMAT & DOCUMENT CONTROL | Design basis documents (process design basis, utility summary, effluent summary) reflected on the drawings. | ASSIST
F-1.12 | Part A — Feed Stage | 1. GENERAL — DRAWING SET-UP, FORMAT & DOCUMENT CONTROL | Sufficient white space / sheet allocation for expected detail-engineering development (drawings not already overcrowded). | ASSIST
F-2.1 | Part A — Feed Stage | 2. PROCESS DESIGN DEFINITION | All operating modes identified (normal, startup, shutdown, regeneration, turndown, alternative feeds) and the P&ID supports each. | HUMAN
F-2.2 | Part A — Feed Stage | 2. PROCESS DESIGN DEFINITION | Process flow path complete and correct from battery limit to battery limit for every service. | HUMAN
F-2.3 | Part A — Feed Stage | 2. PROCESS DESIGN DEFINITION | Line sizing basis established: preliminary sizes shown for all major process lines, consistent with hydraulic calculations. | HUMAN
F-2.4 | Part A — Feed Stage | 2. PROCESS DESIGN DEFINITION | Design pressure and temperature philosophy established and applied consistently (margins above operating, hierarchy across systems). | HUMAN
F-2.5 | Part A — Feed Stage | 2. PROCESS DESIGN DEFINITION | Turndown and rangeability requirements identified where they drive equipment/instrument selection. | HUMAN
F-2.6 | Part A — Feed Stage | 2. PROCESS DESIGN DEFINITION | Two-phase flow, slug flow, flashing, and erosive/corrosive services identified and flagged for special treatment. | HUMAN
F-2.7 | Part A — Feed Stage | 2. PROCESS DESIGN DEFINITION | Material selection / corrosion study results reflected in preliminary piping classes assigned to each line. | HUMAN
F-2.8 | Part A — Feed Stage | 2. PROCESS DESIGN DEFINITION | Process chemistry hazards (H2S, HF, chlorides, hydrates, fouling, polymerization) identified with notes where they drive design. | HUMAN
F-2.9 | Part A — Feed Stage | 2. PROCESS DESIGN DEFINITION | Utility demand points identified for every consumer, consistent with the utility summary. | HUMAN
F-2.10 | Part A — Feed Stage | 2. PROCESS DESIGN DEFINITION | Effluent, emission, and waste streams identified with disposition routing consistent with the environmental basis. | HUMAN
F-3.1 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | All equipment from the PFD/equipment list is shown with correct tag numbers and service descriptions. | ASSIST
F-3.2 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | Equipment sparing philosophy (duty/standby, 2x50%, 3x50%) resolved and reflected in the configuration shown. | ASSIST
F-3.3 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | Equipment title blocks show FEED-level data: capacity/duty, design P/T, materials — consistent with process datasheets. | ASSIST
F-3.4 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | Major nozzles shown for each equipment item (process, relief, vent, drain, instrument connections at concept level). | ASSIST
F-3.5 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | Vessel elevation requirements shown where process-critical (NPSH, gravity flow, thermosiphon reboilers). | ASSIST
F-3.6 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | Pump configuration defined: type, duty/standby, minimum-flow protection concept, seal plan concept. | ASSIST
F-3.7 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | Compressor configuration defined: stages, anti-surge concept, KO drums, lube/seal systems identified (vendor scope noted). | ASSIST
F-3.8 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | Heat exchanger types selected and consistent with datasheets; bypass requirements for control identified. | ASSIST
F-3.9 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | Fired equipment shown with fuel system, BMS interface concept, and safeguarding connections identified. | ASSIST
F-3.10 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | Storage tanks shown with blanketing/venting concept per API 2000 basis and overfill protection philosophy. | ASSIST
F-3.11 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | Packaged/licensed units shown as defined battery-limit boxes with interface streams tagged; vendor scope clouded or noted. | ASSIST
F-3.12 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | Long-lead equipment fully defined on the P&ID to the level needed for purchase specification. | ASSIST
F-3.13 | Part A — Feed Stage | 3. EQUIPMENT CONFIGURATION & DATA | Future/spare equipment provisions shown where required by the design basis (space, valved connections, 'FUTURE' labels). | ASSIST
F-4.1 | Part A — Feed Stage | 4. PIPING & LAYOUT-CRITICAL REQUIREMENTS | Line numbering system established and every line carries a unique number consistent with the FEED line list. | ASSIST
F-4.2 | Part A — Feed Stage | 4. PIPING & LAYOUT-CRITICAL REQUIREMENTS | Preliminary piping classes/specs assigned to all lines; spec-break philosophy defined (even if exact locations are detail-stage). | ASSIST
F-4.3 | Part A — Feed Stage | 4. PIPING & LAYOUT-CRITICAL REQUIREMENTS | Flow direction arrows on all lines and consistent with process intent in all operating modes. | HUMAN
F-4.4 | Part A — Feed Stage | 4. PIPING & LAYOUT-CRITICAL REQUIREMENTS | Layout-critical piping requirements noted: slope, no-pocket, free-draining, minimum length, symmetry (reboilers, relief, compressor suction). | ASSIST
F-4.5 | Part A — Feed Stage | 4. PIPING & LAYOUT-CRITICAL REQUIREMENTS | Gravity-flow and thermosiphon circuits identified with elevation requirements noted. | ASSIST
F-4.6 | Part A — Feed Stage | 4. PIPING & LAYOUT-CRITICAL REQUIREMENTS | Critical line routing constraints flagged (e.g., 'route without pockets to flare KO drum') for detail engineering. | ASSIST
F-4.7 | Part A — Feed Stage | 4. PIPING & LAYOUT-CRITICAL REQUIREMENTS | Insulation and heat-tracing philosophy established; insulation classes assigned to lines at FEED level. | ASSIST
F-4.8 | Part A — Feed Stage | 4. PIPING & LAYOUT-CRITICAL REQUIREMENTS | Pigging, flushing, and cleaning requirements identified where they affect line configuration (launchers/receivers shown). | ASSIST
F-4.9 | Part A — Feed Stage | 4. PIPING & LAYOUT-CRITICAL REQUIREMENTS | Sample point philosophy defined and major sample points located. | ASSIST
F-4.10 | Part A — Feed Stage | 4. PIPING & LAYOUT-CRITICAL REQUIREMENTS | Chemical injection points identified with injection philosophy (type, location) established. | ASSIST
F-4.11 | Part A — Feed Stage | 4. PIPING & LAYOUT-CRITICAL REQUIREMENTS | Tie-in points to existing facilities identified, numbered, and captured in a preliminary tie-in list. | ASSIST
F-4.12 | Part A — Feed Stage | 4. PIPING & LAYOUT-CRITICAL REQUIREMENTS | Special piping items (SP) philosophy established; known SP items identified. | ASSIST
F-5.1 | Part A — Feed Stage | 5. VALVES & ISOLATION PHILOSOPHY | Project isolation philosophy defined (single valve / DBB / positive isolation criteria by service and rating) and applied consistently. | ASSIST
F-5.2 | Part A — Feed Stage | 5. VALVES & ISOLATION PHILOSOPHY | Block valves shown at battery limits, equipment isolation boundaries, and maintenance envelopes per the philosophy. | ASSIST
F-5.3 | Part A — Feed Stage | 5. VALVES & ISOLATION PHILOSOPHY | Spading/blinding provisions (spectacle blinds, spades) shown where positive isolation philosophy requires them. | ASSIST
F-5.4 | Part A — Feed Stage | 5. VALVES & ISOLATION PHILOSOPHY | Control valve manifold philosophy defined (block/bypass/drain arrangement by size/service) — shown or covered by typical detail. | ASSIST
F-5.5 | Part A — Feed Stage | 5. VALVES & ISOLATION PHILOSOPHY | Actuated on/off valves (ESDV, SDV, MOV) identified with failure positions consistent with the safeguarding concept. | ASSIST
F-5.6 | Part A — Feed Stage | 5. VALVES & ISOLATION PHILOSOPHY | Check valve philosophy applied at pump/compressor discharges, utility/process interfaces, and injection points. | ASSIST
F-5.7 | Part A — Feed Stage | 5. VALVES & ISOLATION PHILOSOPHY | Locked/car-sealed valve philosophy defined for relief paths and critical services (LO/LC/CSO/CSC). | ASSIST
F-5.8 | Part A — Feed Stage | 5. VALVES & ISOLATION PHILOSOPHY | Valve types consistent with preliminary piping classes (no valve types outside the assigned spec). | ASSIST
F-6.1 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | Overall control philosophy documented and reflected: all major control loops shown complete (element, transmitter, controller, final element). | HUMAN
F-6.2 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | Control system architecture defined (BPCS/DCS, SIS/ESD, F&G, package PLCs) and instrument bubbles use correct location symbols. | ASSIST
F-6.3 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | Instrument tag numbering system established; tags unique and consistent with the FEED instrument index. | ASSIST
F-6.4 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | Major control valves shown with failure positions consistent with the safeguarding and control philosophy. | ASSIST
F-6.5 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | Key process alarms and trips identified (H/HH/L/LL) at FEED level, consistent with the preliminary alarm & trip schedule. | ASSIST
F-6.6 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | SIS functions distinguished from BPCS loops; preliminary SIFs identified consistent with HAZOP/LOPA planning. | HUMAN
F-6.7 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | Interlock references shown for defined shutdown functions, consistent with preliminary cause & effect diagrams. | ASSIST
F-6.8 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | Custody transfer / fiscal metering requirements identified with metering concept shown. | ASSIST
F-6.9 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | Analyzer requirements identified (measurement, location concept) even if sample system detail is a HOLD. | ASSIST
F-6.10 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | Flow element types selected where they drive piping design (meter runs, straight lengths flagged). | ASSIST
F-6.11 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | Level instrumentation concept defined for each vessel (technology, bridle/standpipe philosophy). | ASSIST
F-6.12 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | Local indication philosophy (PG/TG/LG) defined — shown or covered by typical/general note. | ASSIST
F-6.13 | Part A — Feed Stage | 6. CONTROL PHILOSOPHY & INSTRUMENTATION (FEED LEVEL) | Control/operability of each operating mode verifiable from the P&ID (startup controls, kickback, warm-up paths). | HUMAN
F-7.1 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | Overpressure protection philosophy documented; every pressure system has an identified protection concept (PSV, design for max pressure, instrumented protection). | HUMAN
F-7.2 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | All relief devices shown with tag numbers and preliminary set pressures consistent with the relief philosophy and design pressures. | HUMAN
F-7.3 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | Governing relief scenarios identified per system (fire, blocked outlet, CV failure, tube rupture) — preliminary relief load estimates support flare sizing. | HUMAN
F-7.4 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | Relief disposition defined for every device (flare, atmosphere, closed drain) per the disposition philosophy. | HUMAN
F-7.5 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | Flare system concept complete: headers, KO drum(s), seal, purge, ignition — sized for the governing FEED relief case. | HUMAN
F-7.6 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | Emergency depressurization (blowdown) philosophy defined; BDVs and restriction orifices shown for systems requiring depressurization. | HUMAN
F-7.7 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | ESD philosophy and shutdown hierarchy defined (unit/plant/total); ESDVs located at battery limits and inventory isolation points. | HUMAN
F-7.8 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | Fire & gas detection philosophy referenced; F&G-initiated actions consistent with the safeguarding concept. | HUMAN
F-7.9 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | Vacuum protection concept defined where credible vacuum scenarios exist. | HUMAN
F-7.10 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | Thermal relief philosophy defined for blocked-in liquid volumes. | HUMAN
F-7.11 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | Safety-critical elevation/layout requirements flagged (flare KO drum slope, PSV tailpipe routing criteria). | HUMAN
F-7.12 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | HAZID actions affecting P&IDs incorporated; drawings ready for HAZOP (all systems complete enough to be noded). | HUMAN
F-7.13 | Part A — Feed Stage | 7. SAFEGUARDING, RELIEF & FLARE CONCEPT | Inherently safer design review outcomes reflected (inventory reduction, substitution, simplification decisions). | HUMAN
F-8.1 | Part A — Feed Stage | 8. VENTS, DRAINS & DISPOSAL CONCEPT | Drain system philosophy defined (open/closed, segregation by service) and headers shown on utility/interconnecting P&IDs. | ASSIST
F-8.2 | Part A — Feed Stage | 8. VENTS, DRAINS & DISPOSAL CONCEPT | Closed drain / blowdown drum concept sized and shown for the governing case. | ASSIST
F-8.3 | Part A — Feed Stage | 8. VENTS, DRAINS & DISPOSAL CONCEPT | Vent disposition philosophy defined (flare vs. atmosphere criteria) and applied to all identified vents. | ASSIST
F-8.4 | Part A — Feed Stage | 8. VENTS, DRAINS & DISPOSAL CONCEPT | Major maintenance drain/vent requirements identified for large equipment (columns, exchanger banks). | ASSIST
F-8.5 | Part A — Feed Stage | 8. VENTS, DRAINS & DISPOSAL CONCEPT | Steam-out / purge / inerting philosophy for equipment preparation defined and connections concept shown. | ASSIST
F-8.6 | Part A — Feed Stage | 8. VENTS, DRAINS & DISPOSAL CONCEPT | Effluent segregation (oily water, chemical, sanitary, storm) consistent with the effluent treatment design basis. | ASSIST
F-9.1 | Part A — Feed Stage | 9. UTILITY SYSTEMS DEFINITION | Utility generation/import capacity consistent with the utility summary (steam levels, CW, IA/PA, N2, fuel gas, power-related consumers). | ASSIST
F-9.2 | Part A — Feed Stage | 9. UTILITY SYSTEMS DEFINITION | Utility distribution P&IDs cover all headers with preliminary sizes; consumers ticked off against the utility summary. | ASSIST
F-9.3 | Part A — Feed Stage | 9. UTILITY SYSTEMS DEFINITION | Steam and condensate system concept complete (levels, letdowns, desuperheaters, condensate recovery, trap philosophy). | ASSIST
F-9.4 | Part A — Feed Stage | 9. UTILITY SYSTEMS DEFINITION | Cooling water supply/return shown to all consumers; exchanger thermal relief philosophy noted. | ASSIST
F-9.5 | Part A — Feed Stage | 9. UTILITY SYSTEMS DEFINITION | Instrument air/plant air segregation and backup philosophy (receivers, N2 backup) defined. | ASSIST
F-9.6 | Part A — Feed Stage | 9. UTILITY SYSTEMS DEFINITION | Nitrogen system users identified; backflow-prevention philosophy at process interfaces defined. | ASSIST
F-9.7 | Part A — Feed Stage | 9. UTILITY SYSTEMS DEFINITION | Fuel gas system concept complete (conditioning, letdown, distribution to consumers). | ASSIST
F-9.8 | Part A — Feed Stage | 9. UTILITY SYSTEMS DEFINITION | Flushing/utility stations philosophy defined and locations concept established. | ASSIST
F-9.9 | Part A — Feed Stage | 9. UTILITY SYSTEMS DEFINITION | Winterization/frost-protection philosophy established for the site climate. | ASSIST
F-10.1 | Part A — Feed Stage | 10. INTERFACES, VENDOR SCOPE & CONSTRUCTABILITY | Interface register established: every battery-limit stream matches the receiving party's data (size, spec, conditions, tag). | ASSIST
F-10.2 | Part A — Feed Stage | 10. INTERFACES, VENDOR SCOPE & CONSTRUCTABILITY | Vendor package battery limits defined with interface concept (process, utility, control) sufficient for enquiry packages. | ASSIST
F-10.3 | Part A — Feed Stage | 10. INTERFACES, VENDOR SCOPE & CONSTRUCTABILITY | Licensor-mandated features preserved; any deviations formally approved and documented. | ASSIST
F-10.4 | Part A — Feed Stage | 10. INTERFACES, VENDOR SCOPE & CONSTRUCTABILITY | Brownfield interfaces verified against as-built documentation; site survey gaps captured as HOLDs. | ASSIST
F-10.5 | Part A — Feed Stage | 10. INTERFACES, VENDOR SCOPE & CONSTRUCTABILITY | Modularization/constructability decisions reflected where they affect P&ID configuration (module boundaries, hook-up spools). | ASSIST
F-10.6 | Part A — Feed Stage | 10. INTERFACES, VENDOR SCOPE & CONSTRUCTABILITY | Preliminary 3D/plot plan review comments affecting P&IDs incorporated (elevation, NPSH, gravity-flow constraints). | ASSIST
F-10.7 | Part A — Feed Stage | 10. INTERFACES, VENDOR SCOPE & CONSTRUCTABILITY | Commissioning and startup provisions identified (temporary strainers, startup bypasses, first-fill connections) at concept level. | ASSIST
F-11.1 | Part A — Feed Stage | 11. CONSISTENCY WITH FEED DELIVERABLES | PFDs / H&MB: configuration, stream data, and equipment fully consistent. | AUTO
F-11.2 | Part A — Feed Stage | 11. CONSISTENCY WITH FEED DELIVERABLES | FEED line list: every line on the P&ID captured with size, preliminary spec, conditions, insulation class. | AUTO
F-11.3 | Part A — Feed Stage | 11. CONSISTENCY WITH FEED DELIVERABLES | Equipment list & process datasheets: tags, duties, design conditions consistent. | ASSIST
F-11.4 | Part A — Feed Stage | 11. CONSISTENCY WITH FEED DELIVERABLES | Preliminary instrument index: all instrument bubbles captured; no orphan tags. | AUTO
F-11.5 | Part A — Feed Stage | 11. CONSISTENCY WITH FEED DELIVERABLES | Preliminary cause & effect / SAFE charts: shutdown functions consistent. | AUTO
F-11.6 | Part A — Feed Stage | 11. CONSISTENCY WITH FEED DELIVERABLES | Relief philosophy report / preliminary relief register: all devices and set pressures reconciled. | AUTO
F-11.7 | Part A — Feed Stage | 11. CONSISTENCY WITH FEED DELIVERABLES | Utility summary and UFDs: consumers and header configuration consistent. | AUTO
F-11.8 | Part A — Feed Stage | 11. CONSISTENCY WITH FEED DELIVERABLES | Cost estimate / MTO basis: P&ID content supports the target estimate class (no known scope missing from drawings). | ASSIST
F-11.9 | Part A — Feed Stage | 11. CONSISTENCY WITH FEED DELIVERABLES | HAZOP preparation: node boundaries markable, drawings frozen/issued at the revision to be used for HAZOP. | HUMAN
F-11.10 | Part A — Feed Stage | 11. CONSISTENCY WITH FEED DELIVERABLES | EPC scope definition: HOLD register, notes, and drawings collectively define what detail engineering must complete. | AUTO
D-1.1 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | Drawing number, title, unit/area, and sheet number are correct and match the drawing index / master document register. | ASSIST
D-1.2 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | Revision number, revision date, revision description, and revision triangles/clouds are shown correctly; superseded clouds from earlier revisions removed. | ASSIST
D-1.3 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | Title block signatures (drawn, checked, approved) are complete and correct for the issue status (IFR/IFD/IFC). | ASSIST
D-1.4 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | Drawing status stamp (e.g., ISSUED FOR CONSTRUCTION) is correct for the current issue. | ASSIST
D-1.5 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | Legend, symbols, and abbreviations conform to the project Legend & Symbols sheets (ISA-5.1 / client standard); no undefined symbols used. | ASSIST
D-1.6 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | Continuation arrows / off-page connectors reference the correct drawing numbers and are consistent in both directions (to/from). | ASSIST
D-1.7 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | Match lines between adjacent P&IDs check correctly — line numbers, sizes, specs, and flow direction consistent across sheets. | ASSIST
D-1.8 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | All HOLD clouds are numbered, listed in the HOLD table, and have a defined close-out action/owner. | ASSIST
D-1.9 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | General notes are applicable, numbered sequentially, and referenced correctly on the drawing body. | ASSIST
D-1.10 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | Cross-references to related documents (line list, equipment list, instrument index, cause & effect, UFD/PFD) are consistent. | ASSIST
D-1.11 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | P&ID reflects the latest PFD/heat & material balance revision; duty/process changes since FEED are incorporated. | ASSIST
D-1.12 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | Drawing is legible at issue scale — no overlapping text, crowded areas split to additional sheets where required. | ASSIST
D-1.13 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | North arrow / plant orientation reference shown where required by project standard. | ASSIST
D-1.14 | Part B — Detail Engineering Stage | 1. GENERAL — DRAWING FORMAT & DOCUMENTATION | Battery limit / scope split boundaries (by contractor, vendor, existing) are clearly shown and labelled. | ASSIST
D-2.1 | Part B — Detail Engineering Stage | 2. EQUIPMENT | All equipment items shown on the PFD and equipment list appear on the P&IDs, with correct tag numbers. | ASSIST
D-2.2 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Equipment tags, service descriptions, and duty/size/capacity data in equipment title blocks match the equipment list and datasheets. | ASSIST
D-2.3 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Design pressure/temperature and operating conditions noted for equipment match datasheets and the line list. | ASSIST
D-2.4 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Equipment nozzles are shown with correct size, rating, and identification; orientation consistent with vendor GA drawings. | ASSIST
D-2.5 | Part B — Detail Engineering Stage | 2. EQUIPMENT | All vendor-supplied nozzles are used or blanked; spare nozzles shown and labelled. | ASSIST
D-2.6 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Equipment internals relevant to process function (demister pads, vortex breakers, distributors, baffles, weirs) are shown. | ASSIST
D-2.7 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Vessel elevations, tangent lines, and levels (HLL/NLL/LLL, alarm and trip levels) are shown where required. | ASSIST
D-2.8 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Pumps: correct configuration (duty/standby), auto-start logic reference, minimum flow protection, casing vents/drains, seal plan and seal support systems shown. | ASSIST
D-2.9 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Compressors/blowers: anti-surge/recycle, lube & seal oil systems, interstage coolers/KO drums shown or referenced to vendor P&IDs. | ASSIST
D-2.10 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Heat exchangers: TEMA type consistent with datasheet; shell/tube side services correct; vents, drains, and thermal relief provided. | ASSIST
D-2.11 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Fired heaters/boilers: fuel gas, pilot, BMS interfaces, decoking/snuffing connections shown or referenced. | ASSIST
D-2.12 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Tanks: blanketing, PVRV/breather valves, overflow, gauging and sampling connections shown per API 2000 requirements. | ASSIST
D-2.13 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Packaged units: battery-limit interfaces match vendor P&IDs; scope split clearly clouded/noted; duplicate tags avoided. | ASSIST
D-2.14 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Equipment insulation/personnel-protection requirements indicated consistent with the insulation specification. | ASSIST
D-2.15 | Part B — Detail Engineering Stage | 2. EQUIPMENT | Spare/future equipment clearly identified with correct valving and spading arrangements. | ASSIST
D-3.1 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Every line has a unique, complete line number (size – service – sequence – spec – insulation) matching the line list. | ASSIST
D-3.2 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Line sizes agree with the line list and hydraulic calculations; size changes shown with reducers at the correct location. | ASSIST
D-3.3 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Piping class/spec breaks are shown at the correct location with the correct spec-break symbol, and rating logic is defensible (block valve + spec break orientation). | HUMAN
D-3.4 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Flow direction arrows shown on all lines and consistent with process intent. | ASSIST
D-3.5 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Design/operating conditions of lines consistent with connected equipment and relief design basis. | ASSIST
D-3.6 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Slope requirements (gravity lines, flare headers, drains) are noted with direction and minimum slope. | ASSIST
D-3.7 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | 'No pocket', 'free draining', 'minimize length', and symmetry requirements noted where process-critical (relief lines, compressor suction, two-phase flow). | ASSIST
D-3.8 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | High-point vents and low-point drains provided per specification (indicated or covered by typical/general note). | ASSIST
D-3.9 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Sample connections shown with correct type (closed-loop sampler where required), valving, and accessibility. | ASSIST
D-3.10 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Utility connections/hose stations (N2, air, steam, water) shown at required locations with correct spec and check valve/isolation arrangements. | ASSIST
D-3.11 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Line continuation between P&IDs: size, spec, insulation, and tracing all consistent at match points. | ASSIST
D-3.12 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Reducers, expanders, and eccentric/concentric requirements noted where relevant (pump suction eccentric FSD/FSU). | ASSIST
D-3.13 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Strainers (permanent/temporary/conical) shown at pump/compressor suctions and control valves as per specification. | ASSIST
D-3.14 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Special piping items (SP items) tagged and listed in the special piping item list. | ASSIST
D-3.15 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Pipe expansion/flexibility items (expansion joints, spring supports flagged as SP) shown where applicable. | ASSIST
D-3.16 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Dead legs avoided or justified; provisions for flushing/pigging shown where required. | ASSIST
D-3.17 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Bypass, warm-up, and startup lines provided where required by operating philosophy. | ASSIST
D-3.18 | Part B — Detail Engineering Stage | 3. PIPING — LINES, SPECS & LAYOUT REQUIREMENTS | Chemical injection points: quill/injector type, isolation, check valve, and accessibility per specification. | ASSIST
D-4.1 | Part B — Detail Engineering Stage | 4. VALVES & MANUAL ISOLATION | All valves shown with correct symbol, size (if different from line), and type per the piping material specification. | ASSIST
D-4.2 | Part B — Detail Engineering Stage | 4. VALVES & MANUAL ISOLATION | Isolation philosophy (single valve, double block & bleed, spade/spectacle blind) meets project/HSE requirements for the service and pressure class. | ASSIST
D-4.3 | Part B — Detail Engineering Stage | 4. VALVES & MANUAL ISOLATION | Spectacle blinds, spades, and spacers shown for maintenance isolation and positive isolation (equipment entry, battery limits). | ASSIST
D-4.4 | Part B — Detail Engineering Stage | 4. VALVES & MANUAL ISOLATION | Valve failure positions (FO/FC/FL) shown for all actuated valves and consistent with cause & effect / safety analysis. | ASSIST
D-4.5 | Part B — Detail Engineering Stage | 4. VALVES & MANUAL ISOLATION | Locked-open (LO) / locked-closed (LC) / car-sealed (CSO/CSC) valves identified per relief path and safety requirements. | ASSIST
D-4.6 | Part B — Detail Engineering Stage | 4. VALVES & MANUAL ISOLATION | Check valves provided where reverse flow must be prevented (pump/compressor discharge, utility connections, injection points). | ASSIST
D-4.7 | Part B — Detail Engineering Stage | 4. VALVES & MANUAL ISOLATION | Control valve manifolds: upstream/downstream block valves, bypass (globe) valve, drain between valves per project standard; handwheel requirement noted. | ASSIST
D-4.8 | Part B — Detail Engineering Stage | 4. VALVES & MANUAL ISOLATION | Vent/drain valves plugged, capped, or blinded per specification. | ASSIST
D-4.9 | Part B — Detail Engineering Stage | 4. VALVES & MANUAL ISOLATION | Valves accessibility/operability considerations noted (chain wheels, extended stems, platforms) where flagged by plot plan review. | HUMAN
D-4.10 | Part B — Detail Engineering Stage | 4. VALVES & MANUAL ISOLATION | Actuated valve accessories (limit switches ZSO/ZSC, solenoids, positioners) shown consistent with instrument index. | ASSIST
D-4.11 | Part B — Detail Engineering Stage | 4. VALVES & MANUAL ISOLATION | PSV isolation valves (inlet/outlet) are full bore, locked open, and interlocked per API 520/526 and project philosophy. | ASSIST
D-4.12 | Part B — Detail Engineering Stage | 4. VALVES & MANUAL ISOLATION | Line blind symbols and 'removable spool' notations shown where positive isolation is achieved by spool removal. | ASSIST
D-5.1 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | All instruments shown with correct ISA tag numbers, unique across the project, and matching the instrument index. | ASSIST
D-5.2 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Instrument bubbles show correct location/accessibility designation (field, local panel, DCS, ESD/SIS) per legend. | ASSIST
D-5.3 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Control loops are complete: sensing element, transmitter, controller, and final element all shown and correctly connected. | ASSIST
D-5.4 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Signal line types (electric, pneumatic, software/data link, capillary) drawn per legend and used consistently. | ASSIST
D-5.5 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Set points, alarm points (H/HH/L/LL), and trip functions shown or referenced to the alarm & trip schedule. | ASSIST
D-5.6 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | SIS/ESD functions clearly distinguished from BPCS (separate tags/logic identifiers, e.g., interlock symbols/SIF numbers), consistent with the cause & effect diagram and SRS. | ASSIST
D-5.7 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Interlock and permissive logic references (I-xxx) shown at all affected devices, matching cause & effect diagrams. | ASSIST
D-5.8 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Control valve data: size, failure position, tightness class where required, and bypass/handjack per datasheet. | ASSIST
D-5.9 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Flow elements: type (orifice, venturi, coriolis, magnetic, ultrasonic), meter runs/straight-length requirements noted. | ASSIST
D-5.10 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Level instruments: type, nozzle locations, standpipes/bridles, gauge glasses visible from operating position; ranges cover alarm/trip levels. | ASSIST
D-5.11 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Pressure/temperature instruments: correct process connections, thermowells shown, test/calibration connections per spec. | ASSIST
D-5.12 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Analyzers: sample take-off, fast loop, sample conditioning, and return/disposal shown or referenced to analyzer P&IDs. | ASSIST
D-5.13 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Instrument isolation, vent, and drain valving (manifolds) per project installation standards. | ASSIST
D-5.14 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Local gauges (PG/TG/LG) provided at required locations (pump discharge, vessel levels, filter dP). | ASSIST
D-5.15 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Instrument air/power supply requirements referenced where relevant (e.g., air failure behavior). | ASSIST
D-5.16 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | MOV/actuated valve torque/thrust or fail-safe accessories consistent with electrical & instrumentation design. | ASSIST
D-5.17 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Field pushbuttons, local panels, and hand switches (HS) shown where required by operating philosophy. | ASSIST
D-5.18 | Part B — Detail Engineering Stage | 5. INSTRUMENTATION & CONTROL | Redundancy/voting (2oo3, 1oo2) of SIS transmitters shown consistent with SIL assessment. | ASSIST
D-6.1 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Every credible overpressure source is protected: PSV/PRV, rupture disc, thermal relief, or documented inherent protection per API 521 study. | HUMAN
D-6.2 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Relief device tag, set pressure, and (where project standard requires) size/orifice designation shown and matching relief datasheets. | ASSIST
D-6.3 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Relief inlet/outlet line sizes match relief sizing calculations (inlet dP ≤ 3%, backpressure limits respected). | ASSIST
D-6.4 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Rupture disc + PSV combinations show burst indication (excess flow/pressure gauge) between disc and valve. | ASSIST
D-6.5 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Discharge routing correct (flare, atmosphere at safe location, closed drain) per disposition philosophy; atmospheric tailpipes per safe-location criteria. | HUMAN
D-6.6 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Flare headers: sloped to KO drum, no pockets, purge (N2/FG) connections, and molecular seal/liquid seal shown as applicable. | ASSIST
D-6.7 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Thermal relief valves provided for blocked-in liquid volumes (long pipe runs, coolers, LPG lines) per project criteria. | ASSIST
D-6.8 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Vacuum protection provided where credible (steam-out, pump-out, cooling of full vessels). | HUMAN
D-6.9 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | PSV bypass/blowdown around relief devices per maintenance philosophy; spare relief valve arrangements correct. | ASSIST
D-6.10 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Emergency depressurization (blowdown) valves, restriction orifices, and routing per API 521 depressurization study. | ASSIST
D-6.11 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Fire case, blocked outlet, control valve failure, and tube rupture scenarios traced and consistent with relief documentation. | ASSIST
D-6.12 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Safety showers/eye washes shown or referenced where hazardous chemicals handled. | ASSIST
D-6.13 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Flame arrestors/detonation arrestors shown where required (atmospheric tanks, vent systems). | ASSIST
D-6.14 | Part B — Detail Engineering Stage | 6. RELIEF, FLARE & SAFETY SYSTEMS | Car seal/interlock strategy on relief path block valves guarantees relief availability in all operating modes. | HUMAN
D-7.1 | Part B — Detail Engineering Stage | 7. VENTS, DRAINS & DISPOSAL SYSTEMS | Process vents routed to correct destination (flare, atmosphere, vent header) per emission/disposition philosophy. | ASSIST
D-7.2 | Part B — Detail Engineering Stage | 7. VENTS, DRAINS & DISPOSAL SYSTEMS | Closed drain and open drain systems segregated correctly (hydrocarbon vs. non-hazardous, hot vs. cold). | ASSIST
D-7.3 | Part B — Detail Engineering Stage | 7. VENTS, DRAINS & DISPOSAL SYSTEMS | Equipment drainage: all vessels/exchangers/pumps drain to appropriate system with adequate valving. | HUMAN
D-7.4 | Part B — Detail Engineering Stage | 7. VENTS, DRAINS & DISPOSAL SYSTEMS | Funnel/tundish connections shown with air gap where required; sealed drains where hazardous. | ASSIST
D-7.5 | Part B — Detail Engineering Stage | 7. VENTS, DRAINS & DISPOSAL SYSTEMS | Maintenance drain/flush/steam-out connections provided for equipment preparation. | ASSIST
D-7.6 | Part B — Detail Engineering Stage | 7. VENTS, DRAINS & DISPOSAL SYSTEMS | Drain headers sloped and sized; seal loops/traps shown where required to prevent gas migration. | ASSIST
D-7.7 | Part B — Detail Engineering Stage | 7. VENTS, DRAINS & DISPOSAL SYSTEMS | Tank/vessel overflow lines routed safely with adequate capacity and correct discharge location. | HUMAN
D-8.1 | Part B — Detail Engineering Stage | 8. UTILITIES, INSULATION & HEAT TRACING | Utility distribution consistent with utility flow diagrams (UFDs); supply/return headers correctly sized and specced. | ASSIST
D-8.2 | Part B — Detail Engineering Stage | 8. UTILITIES, INSULATION & HEAT TRACING | Steam traps shown with correct type/orientation; condensate routed to correct recovery/disposal system. | ASSIST
D-8.3 | Part B — Detail Engineering Stage | 8. UTILITIES, INSULATION & HEAT TRACING | Steam/electric tracing indicated on all lines requiring it per line list; tracing supply/return shown or covered by note. | ASSIST
D-8.4 | Part B — Detail Engineering Stage | 8. UTILITIES, INSULATION & HEAT TRACING | Insulation type and thickness codes (H/C/P/PP etc.) on all lines/equipment match line list and insulation spec. | ASSIST
D-8.5 | Part B — Detail Engineering Stage | 8. UTILITIES, INSULATION & HEAT TRACING | Winterization measures complete for lines subject to freezing (dead legs, instrument legs, intermittent lines). | ASSIST
D-8.6 | Part B — Detail Engineering Stage | 8. UTILITIES, INSULATION & HEAT TRACING | Nitrogen/inert gas connections: check valve + isolation per backflow-prevention standard; no permanent cross-connections between utility and process. | ASSIST
D-8.7 | Part B — Detail Engineering Stage | 8. UTILITIES, INSULATION & HEAT TRACING | Cooling water supply/return: correct flow direction, vents at high points, thermal relief on blocked-in exchangers. | ASSIST
D-8.8 | Part B — Detail Engineering Stage | 8. UTILITIES, INSULATION & HEAT TRACING | Instrument air / plant air segregation correct; air receivers and dryers referenced correctly. | ASSIST
D-8.9 | Part B — Detail Engineering Stage | 8. UTILITIES, INSULATION & HEAT TRACING | Fuel gas conditioning (KO drum, filters, heaters) shown for consumers per vendor requirements. | ASSIST
D-8.10 | Part B — Detail Engineering Stage | 8. UTILITIES, INSULATION & HEAT TRACING | Potable/utility water cross-connection protection (backflow preventers) shown where required. | ASSIST
D-9.1 | Part B — Detail Engineering Stage | 9. PROCESS SAFETY / HAZOP & OPERABILITY | All HAZOP/LOPA/SIL action items affecting this P&ID are incorporated and closed out (verify against action register). | HUMAN
D-9.2 | Part B — Detail Engineering Stage | 9. PROCESS SAFETY / HAZOP & OPERABILITY | Design conforms to overpressure protection philosophy and equipment design-pressure hierarchy (no unprotected LP equipment exposed to HP source). | HUMAN
D-9.3 | Part B — Detail Engineering Stage | 9. PROCESS SAFETY / HAZOP & OPERABILITY | Startup, shutdown, regeneration, and alternative operating modes can be executed with the valving/instrumentation shown. | HUMAN
D-9.4 | Part B — Detail Engineering Stage | 9. PROCESS SAFETY / HAZOP & OPERABILITY | Pressurization/depressurization, purging, and inerting paths available for commissioning and maintenance. | HUMAN
D-9.5 | Part B — Detail Engineering Stage | 9. PROCESS SAFETY / HAZOP & OPERABILITY | Isolation for maintenance meets energy-isolation standard for every maintainable item (pumps, control valves, instruments, exchangers). | HUMAN
D-9.6 | Part B — Detail Engineering Stage | 9. PROCESS SAFETY / HAZOP & OPERABILITY | Adequate provisions to avoid siphoning, backflow, and inadvertent mixing of incompatible services. | HUMAN
D-9.7 | Part B — Detail Engineering Stage | 9. PROCESS SAFETY / HAZOP & OPERABILITY | Relief and blowdown philosophy consistent across all operating modes (including standby equipment lineups). | HUMAN
D-9.8 | Part B — Detail Engineering Stage | 9. PROCESS SAFETY / HAZOP & OPERABILITY | Human factors: critical manual valves and instruments operable/readable from grade/platform (coordinate with plot plan/3D review). | HUMAN
D-9.9 | Part B — Detail Engineering Stage | 9. PROCESS SAFETY / HAZOP & OPERABILITY | Emergency isolation valves (EIV/ESDV/ROSOV) located per fire-safety study; fire-safe valve requirement noted. | HUMAN
D-9.10 | Part B — Detail Engineering Stage | 9. PROCESS SAFETY / HAZOP & OPERABILITY | Hazardous area / material hazard notes (e.g., H2S, HF, hot service) shown where required by project HSE standard. | HUMAN
D-10.1 | Part B — Detail Engineering Stage | 10. TIE-INS, VENDOR PACKAGES & INTERFACES | All tie-in points to existing facilities tagged, listed in the tie-in schedule, and shown with correct isolation/spading. | ASSIST
D-10.2 | Part B — Detail Engineering Stage | 10. TIE-INS, VENDOR PACKAGES & INTERFACES | Tie-in type (hot tap, cold cut, existing valve) and existing line data verified against as-built drawings. | ASSIST
D-10.3 | Part B — Detail Engineering Stage | 10. TIE-INS, VENDOR PACKAGES & INTERFACES | Vendor package battery limits match vendor P&IDs (nozzle sizes, ratings, specs, instrumentation split). | ASSIST
D-10.4 | Part B — Detail Engineering Stage | 10. TIE-INS, VENDOR PACKAGES & INTERFACES | Free-issue vs. vendor-scope instrumentation/valves clearly identified; no gaps or duplications at interfaces. | ASSIST
D-10.5 | Part B — Detail Engineering Stage | 10. TIE-INS, VENDOR PACKAGES & INTERFACES | Interface signals between package unit control panels and plant DCS/SIS referenced consistently. | ASSIST
D-10.6 | Part B — Detail Engineering Stage | 10. TIE-INS, VENDOR PACKAGES & INTERFACES | Future connections shown with correct termination (blind flange, isolation valve, spade) and labelled 'FUTURE'. | ASSIST
D-10.7 | Part B — Detail Engineering Stage | 10. TIE-INS, VENDOR PACKAGES & INTERFACES | Underground/aboveground transition points shown where relevant to scope split. | ASSIST
D-11.1 | Part B — Detail Engineering Stage | 11. CONSISTENCY WITH OTHER ENGINEERING DOCUMENTS | Line list: every line on the P&ID appears in the line list with identical data (size, spec, conditions, insulation, test). | AUTO
D-11.2 | Part B — Detail Engineering Stage | 11. CONSISTENCY WITH OTHER ENGINEERING DOCUMENTS | Equipment list and datasheets: tags, duties, and design conditions consistent. | ASSIST
D-11.3 | Part B — Detail Engineering Stage | 11. CONSISTENCY WITH OTHER ENGINEERING DOCUMENTS | Instrument index and datasheets: every instrument bubble matches index; no orphan tags in either document. | ASSIST
D-11.4 | Part B — Detail Engineering Stage | 11. CONSISTENCY WITH OTHER ENGINEERING DOCUMENTS | Cause & effect diagrams / SAFE chart: all trip functions, interlocks, and final elements consistent. | AUTO
D-11.5 | Part B — Detail Engineering Stage | 11. CONSISTENCY WITH OTHER ENGINEERING DOCUMENTS | Plot plan / 3D model: equipment arrangement, elevations for gravity flow, and NPSH-critical layouts consistent. | ASSIST
D-11.6 | Part B — Detail Engineering Stage | 11. CONSISTENCY WITH OTHER ENGINEERING DOCUMENTS | Electrical single-line/load list: motor tags, MOVs, and electric heaters consistent. | AUTO
D-11.7 | Part B — Detail Engineering Stage | 11. CONSISTENCY WITH OTHER ENGINEERING DOCUMENTS | Isometrics/MTO basis: special items, spec breaks, and insulation limits align with piping deliverables. | AUTO
D-11.8 | Part B — Detail Engineering Stage | 11. CONSISTENCY WITH OTHER ENGINEERING DOCUMENTS | Process safeguarding memorandum / relief register: all relief devices and safeguarding measures reconciled. | AUTO
C-1.1 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | Every off-page connector/continuation arrow points to an existing drawing, and the receiving drawing shows the matching return arrow (check both directions). | AUTO
C-1.2 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | At every match point between sheets: line number, size, piping class, insulation code, and tracing are identical on both drawings. | AUTO
C-1.3 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | Flow direction is consistent across sheet boundaries (no line reversing direction at a match line). | AUTO
C-1.4 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | Design conditions implied on both sides of a continuation are compatible (no silent spec/rating change at the sheet break). | AUTO
C-1.5 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | Equipment shown on multiple sheets (e.g., a column on two sheets) carries identical tag, title-block data, and nozzle allocation. | AUTO
C-1.6 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | No duplicate tag numbers anywhere in the set — lines, equipment, instruments, relief devices, SP items, tie-ins. | AUTO
C-1.7 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | No orphan references: every 'see note X', 'typical detail Y', 'HOLD n', and interlock reference points to something that exists. | AUTO
C-1.8 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | Symbols and abbreviations used match the project legend sheets; the same item type is drawn the same way on every sheet. | AUTO
C-1.9 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | General notes are not contradicted by drawing content on any sheet (e.g., note says 'all drains 3/4 in.' but a 1 in. drain is drawn). | AUTO
C-1.10 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | Typical details, when referenced, actually apply to the location referencing them (correct size range, service, arrangement). | AUTO
C-1.11 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | Revision clouds correspond to actual changes and the revision description; no unclouded changes since the previous issue (spot-check by overlay/compare). | AUTO
C-1.12 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | HOLD clouds on drawings reconcile one-to-one with the HOLD register (no unregistered clouds, no registered HOLDs missing from drawings). | AUTO
C-1.13 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | Interlock/SIF numbers used at initiator and at final element refer to the same function on every sheet where they appear. | AUTO
C-1.14 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | Utility headers on process sheets match the corresponding utility distribution P&ID (size, spec, branch location, valve arrangement). | AUTO
C-1.15 | Part C — Consistency Checks (Internal & Cross-Document) | 1. INTERNAL CONSISTENCY — WITHIN THE P&ID SET | Relief device shown on a process sheet matches its representation on the flare/collection header sheet (tag, tailpipe size, destination). | AUTO
C-2.1 | Part C — Consistency Checks (Internal & Cross-Document) | 2. P&ID vs PFD / HEAT & MATERIAL BALANCE | Every equipment item on the PFD appears on a P&ID and vice versa (no undocumented additions/deletions). | AUTO
C-2.2 | Part C — Consistency Checks (Internal & Cross-Document) | 2. P&ID vs PFD / HEAT & MATERIAL BALANCE | Process configuration (series/parallel, recycle, bypass structure) identical between PFD and P&ID. | AUTO
C-2.3 | Part C — Consistency Checks (Internal & Cross-Document) | 2. P&ID vs PFD / HEAT & MATERIAL BALANCE | Stream routing on P&ID matches PFD stream connectivity; no flow path exists on one and not the other. | AUTO
C-2.4 | Part C — Consistency Checks (Internal & Cross-Document) | 2. P&ID vs PFD / HEAT & MATERIAL BALANCE | Line sizes on P&ID are consistent with H&MB flow rates and the hydraulic calculation basis. | ASSIST
C-2.5 | Part C — Consistency Checks (Internal & Cross-Document) | 2. P&ID vs PFD / HEAT & MATERIAL BALANCE | Operating conditions noted on P&ID (where shown) match the H&MB for the governing case. | AUTO
C-2.6 | Part C — Consistency Checks (Internal & Cross-Document) | 2. P&ID vs PFD / HEAT & MATERIAL BALANCE | Major control loops shown on the PFD (control intent) appear on the P&ID with the same measured/manipulated variables. | AUTO
C-2.7 | Part C — Consistency Checks (Internal & Cross-Document) | 2. P&ID vs PFD / HEAT & MATERIAL BALANCE | Equipment duty/capacity in P&ID title blocks matches PFD/H&MB data. | AUTO
C-2.8 | Part C — Consistency Checks (Internal & Cross-Document) | 2. P&ID vs PFD / HEAT & MATERIAL BALANCE | PFD revision referenced by the P&ID set is the current approved revision. | AUTO
C-3.1 | Part C — Consistency Checks (Internal & Cross-Document) | 3. P&ID vs LINE LIST | Every line number on the P&IDs exists in the line list; every line-list entry appears on a P&ID (two-way check, no orphans either way). | AUTO
C-3.2 | Part C — Consistency Checks (Internal & Cross-Document) | 3. P&ID vs LINE LIST | Line size on drawing = line size in list, for every line including short branches that carry their own number. | AUTO
C-3.3 | Part C — Consistency Checks (Internal & Cross-Document) | 3. P&ID vs LINE LIST | Piping class/spec on drawing = spec in list; spec breaks on the drawing occur where the list changes spec. | AUTO
C-3.4 | Part C — Consistency Checks (Internal & Cross-Document) | 3. P&ID vs LINE LIST | Insulation class and thickness code identical between drawing and list. | AUTO
C-3.5 | Part C — Consistency Checks (Internal & Cross-Document) | 3. P&ID vs LINE LIST | Heat tracing (type: steam/electric) shown on the drawing wherever the list requires it, and not shown where it doesn't. | AUTO
C-3.6 | Part C — Consistency Checks (Internal & Cross-Document) | 3. P&ID vs LINE LIST | Design and operating P/T in the line list are consistent with the systems the line connects to on the P&ID (and with relief protection). | AUTO
C-3.7 | Part C — Consistency Checks (Internal & Cross-Document) | 3. P&ID vs LINE LIST | 'From / To' fields in the line list match the actual origin and destination shown on the drawings. | AUTO
C-3.8 | Part C — Consistency Checks (Internal & Cross-Document) | 3. P&ID vs LINE LIST | Test pressure/test medium and code class fields in the list are consistent with the drawing's spec and service. | AUTO
C-3.9 | Part C — Consistency Checks (Internal & Cross-Document) | 3. P&ID vs LINE LIST | Slope, no-pocket, free-drain and other special requirement flags agree between list and drawing notes. | AUTO
C-4.1 | Part C — Consistency Checks (Internal & Cross-Document) | 4. P&ID vs EQUIPMENT LIST & DATASHEETS | Every equipment tag on the P&IDs exists in the equipment list and vice versa (two-way check). | AUTO
C-4.2 | Part C — Consistency Checks (Internal & Cross-Document) | 4. P&ID vs EQUIPMENT LIST & DATASHEETS | Service description in P&ID title block matches the equipment list wording. | AUTO
C-4.3 | Part C — Consistency Checks (Internal & Cross-Document) | 4. P&ID vs EQUIPMENT LIST & DATASHEETS | Design pressure/temperature in P&ID equipment data matches the mechanical datasheet. | ASSIST
C-4.4 | Part C — Consistency Checks (Internal & Cross-Document) | 4. P&ID vs EQUIPMENT LIST & DATASHEETS | Capacity/duty/size figures on the P&ID match the process datasheet. | ASSIST
C-4.5 | Part C — Consistency Checks (Internal & Cross-Document) | 4. P&ID vs EQUIPMENT LIST & DATASHEETS | Materials of construction noted on the P&ID (where shown) match the datasheet. | ASSIST
C-4.6 | Part C — Consistency Checks (Internal & Cross-Document) | 4. P&ID vs EQUIPMENT LIST & DATASHEETS | Nozzle schedule on the datasheet reconciles with nozzles used on the P&ID (size, rating, service of each nozzle; spares consistent). | ASSIST
C-4.7 | Part C — Consistency Checks (Internal & Cross-Document) | 4. P&ID vs EQUIPMENT LIST & DATASHEETS | Trim/internals shown on the P&ID (demister, vortex breaker, distributor) appear in the datasheet and vice versa. | ASSIST
C-4.8 | Part C — Consistency Checks (Internal & Cross-Document) | 4. P&ID vs EQUIPMENT LIST & DATASHEETS | Insulation / personnel protection requirement on the P&ID matches the datasheet and insulation schedule. | ASSIST
C-4.9 | Part C — Consistency Checks (Internal & Cross-Document) | 4. P&ID vs EQUIPMENT LIST & DATASHEETS | Equipment design conditions are compatible with the design conditions of all connected lines (no line rated below its equipment without justification). | AUTO
C-5.1 | Part C — Consistency Checks (Internal & Cross-Document) | 5. P&ID vs INSTRUMENT INDEX & DATASHEETS | Every instrument bubble on the P&IDs exists in the instrument index and vice versa (two-way check, including soft tags if project convention includes them). | AUTO
C-5.2 | Part C — Consistency Checks (Internal & Cross-Document) | 5. P&ID vs INSTRUMENT INDEX & DATASHEETS | Tag service descriptions in the index match the P&ID service/location. | AUTO
C-5.3 | Part C — Consistency Checks (Internal & Cross-Document) | 5. P&ID vs INSTRUMENT INDEX & DATASHEETS | Instrument type per index (e.g., vortex FT vs. coriolis) matches the P&ID symbol and any type note. | AUTO
C-5.4 | Part C — Consistency Checks (Internal & Cross-Document) | 5. P&ID vs INSTRUMENT INDEX & DATASHEETS | P&ID location symbol (field / local panel / DCS / SIS) matches the index system allocation for every tag. | AUTO
C-5.5 | Part C — Consistency Checks (Internal & Cross-Document) | 5. P&ID vs INSTRUMENT INDEX & DATASHEETS | Line number/size and equipment tag referenced in the index for each instrument match where the instrument is actually drawn. | AUTO
C-5.6 | Part C — Consistency Checks (Internal & Cross-Document) | 5. P&ID vs INSTRUMENT INDEX & DATASHEETS | Control valve datasheets: tag, size, failure position, and line spec consistent with the P&ID. | ASSIST
C-5.7 | Part C — Consistency Checks (Internal & Cross-Document) | 5. P&ID vs INSTRUMENT INDEX & DATASHEETS | I/O type implied by the P&ID (indication only vs. control vs. trip) matches the index signal/function columns. | AUTO
C-5.8 | Part C — Consistency Checks (Internal & Cross-Document) | 5. P&ID vs INSTRUMENT INDEX & DATASHEETS | Alarm and trip functions on the P&ID (H/HH/L/LL flags) match the alarm & trip schedule set-point list. | AUTO
C-5.9 | Part C — Consistency Checks (Internal & Cross-Document) | 5. P&ID vs INSTRUMENT INDEX & DATASHEETS | Thermowell/process connection details implied on the P&ID consistent with installation datasheets. | ASSIST
C-6.1 | Part C — Consistency Checks (Internal & Cross-Document) | 6. P&ID vs CAUSE & EFFECT / SIS DOCUMENTATION | Every initiator (transmitter/switch) in the C&E diagram appears on the P&ID with matching tag and trip designation (HH/LL). | AUTO
C-6.2 | Part C — Consistency Checks (Internal & Cross-Document) | 6. P&ID vs CAUSE & EFFECT / SIS DOCUMENTATION | Every final element (SDV, BDV, motor trip) in the C&E appears on the P&ID with matching tag and failure position. | AUTO
C-6.3 | Part C — Consistency Checks (Internal & Cross-Document) | 6. P&ID vs CAUSE & EFFECT / SIS DOCUMENTATION | Interlock/SIF numbers on the P&ID match the C&E and SRS numbering one-to-one. | AUTO
C-6.4 | Part C — Consistency Checks (Internal & Cross-Document) | 6. P&ID vs CAUSE & EFFECT / SIS DOCUMENTATION | Voting architecture shown on the P&ID (e.g., 2oo3 transmitters drawn) matches the SRS/SIL calculation basis. | ASSIST
C-6.5 | Part C — Consistency Checks (Internal & Cross-Document) | 6. P&ID vs CAUSE & EFFECT / SIS DOCUMENTATION | Failure positions (FO/FC) on the P&ID produce the safe state defined in the C&E for every trip scenario. | AUTO
C-6.6 | Part C — Consistency Checks (Internal & Cross-Document) | 6. P&ID vs CAUSE & EFFECT / SIS DOCUMENTATION | No shutdown function exists on the P&ID that is absent from the C&E, and vice versa. | AUTO
C-6.7 | Part C — Consistency Checks (Internal & Cross-Document) | 6. P&ID vs CAUSE & EFFECT / SIS DOCUMENTATION | Reset/bypass/override provisions (MOS/POS) referenced consistently between P&ID notes and SIS documentation. | AUTO
C-6.8 | Part C — Consistency Checks (Internal & Cross-Document) | 6. P&ID vs CAUSE & EFFECT / SIS DOCUMENTATION | Package unit trips (vendor C&E) reconcile with plant C&E and with the interface signals shown on the P&ID. | ASSIST
C-7.1 | Part C — Consistency Checks (Internal & Cross-Document) | 7. P&ID vs RELIEF DOCUMENTATION | Every relief device on the P&IDs exists in the relief register/datasheets and vice versa (two-way check). | ASSIST
C-7.2 | Part C — Consistency Checks (Internal & Cross-Document) | 7. P&ID vs RELIEF DOCUMENTATION | Set pressures on the P&ID match relief datasheets and do not exceed the design pressure of the protected system per the line list/equipment datasheets. | ASSIST
C-7.3 | Part C — Consistency Checks (Internal & Cross-Document) | 7. P&ID vs RELIEF DOCUMENTATION | Orifice designation/size on the P&ID (where shown) matches the sizing calculation. | ASSIST
C-7.4 | Part C — Consistency Checks (Internal & Cross-Document) | 7. P&ID vs RELIEF DOCUMENTATION | Inlet and outlet line sizes on the P&ID match the relief calculation's assumed sizes (3% inlet loss, backpressure basis). | ASSIST
C-7.5 | Part C — Consistency Checks (Internal & Cross-Document) | 7. P&ID vs RELIEF DOCUMENTATION | Discharge destination on the P&ID (flare/atm/closed drain) matches the disposition listed in the relief register. | AUTO
C-7.6 | Part C — Consistency Checks (Internal & Cross-Document) | 7. P&ID vs RELIEF DOCUMENTATION | Protected-system boundary assumed in the relief calculation matches the actual isolatable boundary drawn on the P&ID (block valve positions, check valves, car seals). | ASSIST
C-7.7 | Part C — Consistency Checks (Internal & Cross-Document) | 7. P&ID vs RELIEF DOCUMENTATION | Car-seal/lock status of valves in every relief path on the P&ID matches the relief philosophy and register. | AUTO
C-7.8 | Part C — Consistency Checks (Internal & Cross-Document) | 7. P&ID vs RELIEF DOCUMENTATION | Rupture disc / PSV combinations drawn as per datasheet configuration (disc upstream, burst indication, spacer). | ASSIST
C-7.9 | Part C — Consistency Checks (Internal & Cross-Document) | 7. P&ID vs RELIEF DOCUMENTATION | Flare header segment sizes on P&IDs match the flare system sizing report; KO drum and seal data consistent with datasheets. | ASSIST
C-7.10 | Part C — Consistency Checks (Internal & Cross-Document) | 7. P&ID vs RELIEF DOCUMENTATION | Depressurization valves and restriction orifices match the blowdown study (RO bore, BDV size, segment inventory boundaries). | ASSIST
C-8.1 | Part C — Consistency Checks (Internal & Cross-Document) | 8. P&ID vs PIPING SPECS, VALVE SPECS & SP ITEMS | Every piping class code used on the P&IDs exists in the project piping material specification. | AUTO
C-8.2 | Part C — Consistency Checks (Internal & Cross-Document) | 8. P&ID vs PIPING SPECS, VALVE SPECS & SP ITEMS | Valve types drawn are available in the assigned piping class (no gate valve drawn where the spec has none for that size/rating). | AUTO
C-8.3 | Part C — Consistency Checks (Internal & Cross-Document) | 8. P&ID vs PIPING SPECS, VALVE SPECS & SP ITEMS | Spec-break locations follow the spec-break philosophy (correct side of block valve, rating direction) at every occurrence. | AUTO
C-8.4 | Part C — Consistency Checks (Internal & Cross-Document) | 8. P&ID vs PIPING SPECS, VALVE SPECS & SP ITEMS | All special piping items (SP) on the drawings exist in the SP item list with matching tag and description, and vice versa. | AUTO
C-8.5 | Part C — Consistency Checks (Internal & Cross-Document) | 8. P&ID vs PIPING SPECS, VALVE SPECS & SP ITEMS | Branch sizes/types implied by the drawing are permitted by the spec branch table (or flagged as SP). | AUTO
C-8.6 | Part C — Consistency Checks (Internal & Cross-Document) | 8. P&ID vs PIPING SPECS, VALVE SPECS & SP ITEMS | Flange ratings implied at equipment nozzles are compatible with the connecting line class. | AUTO
C-8.7 | Part C — Consistency Checks (Internal & Cross-Document) | 8. P&ID vs PIPING SPECS, VALVE SPECS & SP ITEMS | Instrument connection sizes/types per drawing match the piping spec's instrument connection standard. | AUTO
C-9.1 | Part C — Consistency Checks (Internal & Cross-Document) | 9. P&ID vs PLOT PLAN / 3D MODEL / ISOMETRICS | Relative equipment elevations required by the P&ID (gravity flow, thermosiphon, barometric legs, NPSH) are achieved in the plot plan/3D model. | ASSIST
C-9.2 | Part C — Consistency Checks (Internal & Cross-Document) | 9. P&ID vs PLOT PLAN / 3D MODEL / ISOMETRICS | Slope and no-pocket requirements on the P&ID are achievable in the modeled routing (verify flagged critical lines in 3D). | ASSIST
C-9.3 | Part C — Consistency Checks (Internal & Cross-Document) | 9. P&ID vs PLOT PLAN / 3D MODEL / ISOMETRICS | Line lengths critical to process (pump suction, relief inlet, compressor suction) consistent between P&ID intent and model routing. | ASSIST
C-9.4 | Part C — Consistency Checks (Internal & Cross-Document) | 9. P&ID vs PLOT PLAN / 3D MODEL / ISOMETRICS | Valve accessibility/operability flags on the P&ID (chain wheel, extended stem, platform) reflected in the 3D model review actions. | HUMAN
C-9.5 | Part C — Consistency Checks (Internal & Cross-Document) | 9. P&ID vs PLOT PLAN / 3D MODEL / ISOMETRICS | P&ID-required items appear in isometrics: every valve, SP item, spec break, vent, drain, and instrument connection on the checked line. | ASSIST
C-9.6 | Part C — Consistency Checks (Internal & Cross-Document) | 9. P&ID vs PLOT PLAN / 3D MODEL / ISOMETRICS | Insulation limits on isometrics match P&ID/line-list insulation extents. | ASSIST
C-9.7 | Part C — Consistency Checks (Internal & Cross-Document) | 9. P&ID vs PLOT PLAN / 3D MODEL / ISOMETRICS | Field-routed small-bore philosophy consistent between P&ID notes and piping deliverable scope (nothing falls between the two). | ASSIST
C-10.1 | Part C — Consistency Checks (Internal & Cross-Document) | 10. P&ID vs VENDOR / PACKAGE DOCUMENTATION | Battery-limit interface table: every stream crossing the package boundary matches vendor P&ID (size, rating, spec, flow direction, tag). | ASSIST
C-10.2 | Part C — Consistency Checks (Internal & Cross-Document) | 10. P&ID vs VENDOR / PACKAGE DOCUMENTATION | Vendor-supplied instrumentation and valves within the package match plant P&ID representation (or are correctly shown as vendor scope). | ASSIST
C-10.3 | Part C — Consistency Checks (Internal & Cross-Document) | 10. P&ID vs VENDOR / PACKAGE DOCUMENTATION | No scope gaps or duplications: every interface item is in exactly one party's scope (check against division-of-responsibility document). | ASSIST
C-10.4 | Part C — Consistency Checks (Internal & Cross-Document) | 10. P&ID vs VENDOR / PACKAGE DOCUMENTATION | Vendor nozzle orientations/sizes on certified drawings match the plant P&ID connections. | ASSIST
C-10.5 | Part C — Consistency Checks (Internal & Cross-Document) | 10. P&ID vs VENDOR / PACKAGE DOCUMENTATION | Utility requirements per vendor data (flows, pressures, connection sizes) match the utility connections drawn on plant P&IDs. | ASSIST
C-10.6 | Part C — Consistency Checks (Internal & Cross-Document) | 10. P&ID vs VENDOR / PACKAGE DOCUMENTATION | Vendor relief devices discharging into plant systems are included in plant flare/vent load summation and drawn on the header P&IDs. | ASSIST
C-10.7 | Part C — Consistency Checks (Internal & Cross-Document) | 10. P&ID vs VENDOR / PACKAGE DOCUMENTATION | Interface signals (hardwired/serial) between package panel and plant DCS/SIS consistent between vendor drawings and plant P&ID/C&E. | ASSIST
C-11.1 | Part C — Consistency Checks (Internal & Cross-Document) | 11. P&ID vs ELECTRICAL & OTHER DISCIPLINE DOCUMENTS | Every motor-driven equipment tag on the P&IDs appears in the electrical load list with matching tag and rating basis. | AUTO
C-11.2 | Part C — Consistency Checks (Internal & Cross-Document) | 11. P&ID vs ELECTRICAL & OTHER DISCIPLINE DOCUMENTS | MOVs on the P&IDs appear in the load list and the MOV schedule; failure/stayput behavior consistent. | AUTO
C-11.3 | Part C — Consistency Checks (Internal & Cross-Document) | 11. P&ID vs ELECTRICAL & OTHER DISCIPLINE DOCUMENTS | Electric heaters/tracing on P&IDs reconcile with the electrical load list and heat-tracing schedule. | AUTO
C-11.4 | Part C — Consistency Checks (Internal & Cross-Document) | 11. P&ID vs ELECTRICAL & OTHER DISCIPLINE DOCUMENTS | Hazardous area classification drawings consistent with sources of release implied by the P&ID (vents, drains, sample points). | AUTO
C-11.5 | Part C — Consistency Checks (Internal & Cross-Document) | 11. P&ID vs ELECTRICAL & OTHER DISCIPLINE DOCUMENTS | Cathodic protection/earthing special requirements noted on P&IDs (e.g., insulating joints) match the electrical design. | AUTO
C-11.6 | Part C — Consistency Checks (Internal & Cross-Document) | 11. P&ID vs ELECTRICAL & OTHER DISCIPLINE DOCUMENTS | Civil/structural interfaces flagged on P&IDs (loading racks, sumps, containment) consistent with civil drawings. | AUTO
C-12.1 | Part C — Consistency Checks (Internal & Cross-Document) | 12. P&ID vs UTILITY SUMMARY / UFDs | Every utility consumer on process P&IDs appears in the utility summary with matching demand basis. | AUTO
C-12.2 | Part C — Consistency Checks (Internal & Cross-Document) | 12. P&ID vs UTILITY SUMMARY / UFDs | Utility header sizes and configuration on distribution P&IDs match the UFDs and utility balance. | AUTO
C-12.3 | Part C — Consistency Checks (Internal & Cross-Document) | 12. P&ID vs UTILITY SUMMARY / UFDs | Steam level (HP/MP/LP) supplied to each consumer matches the utility summary allocation. | AUTO
C-12.4 | Part C — Consistency Checks (Internal & Cross-Document) | 12. P&ID vs UTILITY SUMMARY / UFDs | Condensate routing per P&ID matches the condensate balance/recovery scheme. | AUTO
C-12.5 | Part C — Consistency Checks (Internal & Cross-Document) | 12. P&ID vs UTILITY SUMMARY / UFDs | Nitrogen, instrument air, and fuel gas consumers reconcile two-way between P&IDs and the respective balances. | AUTO
C-13.1 | Part C — Consistency Checks (Internal & Cross-Document) | 13. P&ID vs TIE-IN SCHEDULE & AS-BUILT DOCUMENTATION (BROWNFIELD) | Every tie-in symbol on the P&IDs exists in the tie-in schedule and vice versa (two-way check, matching tag numbers). | AUTO
C-13.2 | Part C — Consistency Checks (Internal & Cross-Document) | 13. P&ID vs TIE-IN SCHEDULE & AS-BUILT DOCUMENTATION (BROWNFIELD) | Existing line data at each tie-in (size, spec, service, conditions) verified against as-built P&IDs and site survey. | ASSIST
C-13.3 | Part C — Consistency Checks (Internal & Cross-Document) | 13. P&ID vs TIE-IN SCHEDULE & AS-BUILT DOCUMENTATION (BROWNFIELD) | Tie-in type (hot tap / cold cut / existing valve / existing blind) consistent between drawing and schedule. | AUTO
C-13.4 | Part C — Consistency Checks (Internal & Cross-Document) | 13. P&ID vs TIE-IN SCHEDULE & AS-BUILT DOCUMENTATION (BROWNFIELD) | Isolation and spading requirements for tie-in execution shown consistently on drawing and schedule. | AUTO
C-13.5 | Part C — Consistency Checks (Internal & Cross-Document) | 13. P&ID vs TIE-IN SCHEDULE & AS-BUILT DOCUMENTATION (BROWNFIELD) | Existing equipment/line tags reused on new P&IDs match the as-built numbering system exactly. | ASSIST
C-13.6 | Part C — Consistency Checks (Internal & Cross-Document) | 13. P&ID vs TIE-IN SCHEDULE & AS-BUILT DOCUMENTATION (BROWNFIELD) | Demolition scope: items shown 'to be removed' consistent between demolition P&IDs and the new-works drawings. | AUTO
C-14.1 | Part C — Consistency Checks (Internal & Cross-Document) | 14. CHANGE MANAGEMENT, HAZOP ACTIONS & HOLD CLOSE-OUT | Every HAZOP/LOPA action marked 'implement on P&ID' in the action register is visibly incorporated on the current revision (verify item by item). | HUMAN
C-14.2 | Part C — Consistency Checks (Internal & Cross-Document) | 14. CHANGE MANAGEMENT, HAZOP ACTIONS & HOLD CLOSE-OUT | Every management-of-change (MoC) affecting this unit since the last issue is reflected on the P&IDs. | ASSIST
C-14.3 | Part C — Consistency Checks (Internal & Cross-Document) | 14. CHANGE MANAGEMENT, HAZOP ACTIONS & HOLD CLOSE-OUT | Design change notices/queries (DCN/TQ) affecting P&IDs are incorporated and closed, with the revision cloud referencing them where required. | ASSIST
C-14.4 | Part C — Consistency Checks (Internal & Cross-Document) | 14. CHANGE MANAGEMENT, HAZOP ACTIONS & HOLD CLOSE-OUT | HOLD register: each HOLD closed since last issue has its cloud removed and the resolving information incorporated. | ASSIST
C-14.5 | Part C — Consistency Checks (Internal & Cross-Document) | 14. CHANGE MANAGEMENT, HAZOP ACTIONS & HOLD CLOSE-OUT | Squad-check comments from all disciplines on the previous issue are incorporated or formally rejected with response. | ASSIST
C-14.6 | Part C — Consistency Checks (Internal & Cross-Document) | 14. CHANGE MANAGEMENT, HAZOP ACTIONS & HOLD CLOSE-OUT | The set of documents used for this consistency check are all at their current approved revision (record revisions on the Cover sheet). | ASSIST

## Summary
AI CHECK REGISTER — RESULTS SUMMARY
Group | Checks | Pass | Fail | N/A | Not Checked | No Result | % Executed
Part A — FEED Stage | 113 | 1 | 0 | 0 | 0 | 112 | 0.885%
Part B — Detail Engineering | 133 | 0 | 0 | 0 | 0 | 133 | 0%
Part C — Consistency Checks | 112 | 0 | 0 | 0 | 0 | 112 | 0%
AUTO checks | 83 | 0 | 0 | 0 | 0 | 83 | 0%
ASSIST checks | 226 | 1 | 0 | 0 | 0 | 225 | 0.4425%
HUMAN checks | 49 | 0 | 0 | 0 | 0 | 49 | 0%
TOTAL (all checks) | 358 | 1 | 0 | 0 | 0 | 357 | 0.2793%
Rows 4–6 group by Part (column B of the register); rows 7–9 group by AI feasibility (column E). Register is complete when 'No Result' = 0 for AUTO and ASSIST groups, and every Fail / Not Checked row carries an engineer disposition.